SPECIFICATION

Sections 05810 / 07102 / 07915

PyroFlex Fire Barrier System - PF Series

Dynamic Movement Fire Barrier Sealing System

Architectural Expansion Joints

# PART 1 – GENERAL

  - Work Included

- The work shall consist of furnishing and installing fire barrier assemblies in conjunction with associated architectural expansion joints and in accordance with the details shown on the plans and the requirements of the specifications.  The fire barrier assemblies shall accommodate thermal, seismic and lateral shear movement.  System shall be tested to meet specified endurance ratings. This specification supersedes section 07842 for dynamic movement requirements.

- Related Work

- Section 03300 - Cast-in-place concrete

- Section 05500 - miscellaneous metal / expansion joints

- Section 07600 - Flashing and sheet metal

- Section 07842 – Fire Stopping

  - Submittals

- General – Submit the following according to Division 1 Specification Section.

- Standard Drawings – Submit typical fire barrier and expansion joint drawings(s) indicating pertinent dimensions, general construction, joint opening dimensions and product information.

- Fire Barrier Listing - Submit nationally recognized independent laboratory published listing or certification letter confirming product meets required test standards and fire endurance ratings.

  - Product Delivery, Storage and Handling

- Deliver products to site in Manufacturer’s original, intact, labeled containers and store under cover in a dry location until installed.  Never allow the fire barrier systems to become wet. Store off the ground in temperatures above 40ºF, protect from weather and construction activities.

  - Basis of Design

- All fire barriers shall be designed to meet the specified performance criteria of the project as manufactured by MM Systems Corp., 50 MM Way, Pendergrass, GA, 30567 / Tel. 800-241-3460 or 706-824-7500 / Fax. 706.824.7501       Web: www.mmsystemscorp.com

- Alternate manufacturers will not be considered for this project due to insufficient product evaluation time. Submit for future evaluation, products that meet the design criteria and exhibit performance features that are equal to or superior to those called for in the base product specification.

Submittal of alternates must be made two weeks prior to bid opening on future projects to allow proper evaluation time. Submit nationally recognized laboratory certified listing confirming that proposed fire barrier system meets all required test standards and fire endurance ratings. Manufacturer’s self-written opinion and/or certification letters will not be accepted.

Alternate products not adhering to all listed design features will not be considered. Final decision will be at the sole discretion of the architect or consulting engineer.

## Quality Assurance

- Pre-construction – the General Contractor, Engineer/Architect, Concrete Subcontractor, Manufacturer’s Representative and Installation Contractor, will conduct a pre-construction meeting to discuss joint gap construction, joint width settings and construction phasing. This meeting shall be held prior to any concrete placement and/or wall construction at expansion joint locations.

- Joint Opening Adjustment – the Project Engineer shall provide calculations to the concrete subcontractor to adjust the nominal joint opening the day of the concrete placement. Use a “temperature adjustment table” with expansion joint openings calculated in five (5ºF) degree increments based on a temperature range of [adjust for project] -20ºF to 120ºF.

- Pre-installation Inspection – the General Contractor, Engineer/Architect, Manufacturer’s Representative and Certified Contractor, will conduct a pre-installation project site inspection. The General Contractor shall provide a field report that summarizes the project conditions and any remedial action necessary to correct field conditions (surrounding fire rated construction, substrate, joint size, blockout, vertical offsets, etc.) that may affect fire barrier or expansion joint system performance.

- Service Condition - insure that anticipated service conditions (associated expansion joint, waterproofing, changes in direction, endurance rating, etc) are part of the fire barrier system selection criteria.

- Installation – contractor shall contact manufacturer for detailed installation instructions for the specified fire barrier system. The contractor shall provide proof of contact with manufacturer to insure life-safety guidelines are met.

## PART 2 – PRODUCT

  - General

- Provide fire-resistive barrier system that has been designed to provide the required fire endurance rating, minimize passage of smoke and accommodate dynamic movement without stress or degradation to its components.

- Furnish approved PyroFlex Fire Barrier Sealing System “PF Series – Architectural Joints” as manufactured by MM Systems.  Systems requiring fire resistive caulking will not be permitted.

- Provide certification by an accredited third party witnessing agency certifying that the fire barrier system has been tested in accordance with ASTM E1966 and UL 2079 at a maximum joint opening as defined by ASTM E1399 which meets or exceeds the maximum joint opening required by the project design requirements.

- System and manufacturer must be listed with an accredited independent laboratory. Provide accredited listing showing that the system has been tested and meets the requirements of ASTM E1966, UL 2079, International Building Code Section 713.3.

- Fire barrier shall be cycle tested full length incorporating splice transitions. Provide fire barrier system that meets the following dynamic movement requirements (cpm = cycles per minute):

e.1.1 	Seismic movement rating of 30 (cpm) for 100 cycles, followed by;

e.1.2		Thermal movement rating of 10 (cpm) for 400 cycles.

e.1.3		Total Cycles Required - 500 cycles.

- Supply fire-resistive barrier systems that have ratings equal to or greater than the rating of adjacent construction when tested in accordance with the aforementioned standards. Provide specified [1, 2, 3 or 4] hour rated fire barrier expansion joint assembly for floors and/or specified [1, 2 or 3] hour rated fire barrier expansion joint assembly for walls.

- The contractor must provide written confirmation, utilizing manufacturer’s product data, that the fire barrier selected will accommodate the specified expansion and contraction throughout the full movement cycle.

  - Components and Materials

- PyroFlex Fire Barrier – material shall be a flexible, high purity ceramic fiber blanket. Includes stainless steel foil, intumescent matrix and fire resistive cloth as required to achieve desired protection and endurance rating.

- Metal Attachment Retainer (as required by project conditions)  - shall be preformed metal profile with manufacturer’s standard hardware and fasteners to provide proper attachment of fire barrier assembly to adjoining construction.

- Accessories - Provide necessary assembly hardware, splice transition pieces and anchors required for complete installation.

  - Fabrication

- Ship manufacturer’s standard assembly for the required hourly rating with ends prepared for field splicing.

- Assemblies shall be cut in the field to exact length. Transitions shall be made in the field to accommodate changes in direction.

## PART 3 – EXECUTION

  - Installation

- Preparation of the Work Area

- The contractor shall provide properly formed expansion joint openings constructed to the exact dimensions and elevations shown on manufacturer’s standard system drawings or as shown on the contract drawings. Deviations from these dimensions will not be allowed without the written consent.

- The contractor shall insure that the joint opening sidewall interfaces run parallel to each other for the entire length of the joint.  Sidewalls should be plumb and interfaces must be continuously equidistant from each other across the joint width to accommodate the proper installation of the fire barrier sealing system.

- The contractor shall clean the joint opening of all contaminants prior to installation of the fire barrier system.  Concrete form release agents, water repellents, laitance, surface dirt, rust, old sealants and other protective coatings are examples of materials that must be removed from the joint opening substrate in order to obtain the proper endurance rating.

- All cracks in areas adjacent to the joint must be repaired per the joint manufacturer’s recommendations.

- Installation of the Fire Barrier System

- Fire barrier assembly shall be installed to the specified width of expansion joint opening as per the contract documents and accredited listing authority. Deviations in width shall be brought to the attention of the architect and manufacturer prior to installation of any material. Failure to do so may void fire endurance certification of the assembly.

- Upon completion of installation inspect all splices to ensure they meet with the manufacturer’s instructions.

- Refer to Manufacturers Installation Guide for detailed step-by-step instructions on how to install the fire barrier assembly, metal attachment retainers, splice kits and other components.

  - Clean and Protect

- Protect the fire barrier system and its components during construction. Never allow the fire barrier systems to become wet. Heavy construction vehicles will not be permitted to cross the expansion joint or fire barrier assembly. Clean and remove any debris that is observed at the base of the fire barrier void prior to installation of expansion joint system. Subsequent damage to the fire barrier system will be repaired at the general contractor’s expense.

END OF SECTION