SPECIFICATION

Sections 07 90 00 and 07 95 00

(Formerly Sections 05810 / 07102 / 07915)

Seismic No-bump Slide Plate System

###### SNB Series – Traffic Bearing Expansion Joint

# PART 1 – GENERAL

  - Work Included

- The work shall consist of furnishing and installing seismic expansion joints in accordance with the details shown on the plans and the requirements of the specifications.  The expansion joints utilize recessed extension plates that allow a seismic slide plate to remain flush with finished floor surface. A seismic centering device with impact dampers and displacement springs allow the slide plate to displace and return to its natural position after a seismic occurrence. Watertightness is achieved through an integral flexible fabric reinforced rubber gutter.

- Related Work

- Section 03300 - Cast-in-place concrete

- Section 05500 - Miscellaneous metal / expansion joints

- Section 07600 - Flashing and sheet metal

- Section 07900 - Sealants, caulking and waterproofing

  - Submittals

- General – Submit the following according to Division 1 Specification Section.

- Standard Drawings – Submit typical expansion joint drawings indicating pertinent dimensions, general construction, blockout dimensions and product information.

  - Product Delivery, Storage and Handling

- Deliver products to site in Manufacturer’s original, intact, labeled containers and store under cover in a dry location until installed.  Store off the ground in temperatures above 40ºF, protect from weather and construction activities.

  - Basis of Design

- All joints shall be designed to meet the specified performance criteria of the project as manufactured by MM Systems Corp., 50 MM Way, Pendergrass, GA, 30567 / Tel. 800.241.3460 / Fax. 706.824.7501 / Web www.mm-usa.com

- Alternate manufacturers will not be considered for this project due to insufficient product evaluation time. Submit for future evaluation, products that meet the design criteria and exhibit performance features that are equal to or superior to those called for in the base product specification. Submittal of alternates must be made two weeks prior to bid opening on future projects to allow proper evaluation time. Alternate products not adhering to all listed design features will not be considered. Final decision will be at the sole discretion of the architect or consulting engineer.

- Submit verifiable list of prior installations, along with owner contact information, showing successful experience with the proposed systems that must incorporate solid aluminum seismic centering devices (centering bars) and rubber dampers that provide impact, sound and water infiltration resistance.

## Quality Assurance

- Pre-construction – the General Contractor, Engineer/Architect, Concrete Subcontractor, Manufacturer’s Representative and Certified Contractor, will conduct a pre-construction meeting to discuss blockout construction, joint gap settings, concrete elevations, flatness (critical) and construction phasing. This meeting shall be held prior to any concrete placement at expansion joint blockouts and may be held in conjunction with the concrete pre-pour meeting.

- Joint Opening Adjustment – concrete contractor shall follow the temperature adjustment table shown on the contract drawings to properly set the structural joint opening at time of concrete pour. Joint openings are calculated in five (5ºF) degree increments based on a temperature range of -20ºF to 120ºF [adjust for project]. The concrete contractor shall contact the Engineer of Record to confirm adjustment requirements of the nominal joint opening on the day of concrete placement.

- Expansion Joint Blockouts – vibrate all formwork then float and trowel concrete before final cure to remove all air pockets, voids and spalls.

- Leveling Bed - comprised of structural grout is recommended to compensate for elevation changes along the length of the expansion joint. This will require the blockout depth to be set below the system height shown on the drawings.

- Critical Joint Surface Areas - two feet on each side of the expansion joint opening shall be finish graded concrete perpendicular to joint opening creating flush slab-to-slab transition. Elevations on each side of the joint must be identical.

- Pre-installation Inspection – the General Contractor, Engineer/Architect, Manufacturer’s Representative and Certified Contractor, will conduct a pre-installation project site inspection. The General Contractor shall provide a field report that summarizes the project conditions and any remedial action necessary to correct field conditions (substrate, joint size, blockout, vertical offsets, etc.) that may affect expansion joint system performance.

- Service Condition - insure that anticipated service conditions (loads, speed of traffic, movement, vertical offsets, turning lanes, etc) can be accommodated by the specified expansion joint system.

- Certification / Installation – a factory-trained and “certified” contractor shall install the specified expansion joint system. The contractor shall provide proof of certification from manufacturer and proof of participation in manufacturer’s continuing education program. Installer must show evidence of installing specified system in 5 verifiable projects over the past 5 years.

- Warranty – the Manufacturer and Certified Contractor jointly warrant to the Owner that the expansion joint system shall be free from manufacturing, material and installation defects for a period of two (2) years from the date of installation, based on specified movements and subject to the terms and conditions of the manufacturer’s standard written limited warranty. The manufacturer and certified contractor are not liable or responsible for claims due to defects in the concrete. The Certified Contractor and Manufacturer will jointly warrant and provide at no charge, all materials and labor needed to properly repair defective expansion joint within the term of the warranty.

## PART 2 – PRODUCT

  - General

- Furnish approved Seismic Slide Plate System “SSP Series” as manufactured by MM Systems Corporation designed to meet or exceed all expected seismic movement criteria shown on the contract drawings and capable of resisting a minimum differential vertical displacement of 1/2 inch.

- System size at each joint location is based on the movement and design requirements shown in the movement tables on the contract drawings as defined by the structural engineer of record.

- A pre-certified expansion joint installation contractor shall provide written confirmation that the manufacturer’s expansion joint model and size selected will accommodate expansion, contraction, vertical displacement and lateral shear throughout the full movement cycle as defined by the contract drawings.

- Expansion joint must accommodate pedestrian foot traffic with a slip resistant walking surface that complies with ASTM-F1637 Standard Practice for Safe Walking Surfaces and ADA Guideline for allowable range of maximum slope and static coefficient of friction for walking surfaces.

- Manufacturer shall provide an independent third party analysis by a licensed engineer from the state of [list state of project location] validating that the seismic slide plate expansion joint sealing system meets the following loading requirements:

TRAFFIC LOADS

- Vertical wheel service load of 3000 lbs., fatigue load of 2250 lbs. and a collapse load of 4500 lbs. based on a concentrated area of 4.5” by 4.5”.

- Minimum horizontal force equal to 20% of the maximum vertical wheel load applied in combination with the vertical service and fatigue loads to account for vehicle deceleration and acceleration effects.

- Minimum additional vertical load factor of 1.3 allows for dynamic, vibratory and impact effects.

- Designed for equipment and vehicles traveling at low sustained speeds with pneumatic tires.

- Seismic slide plate system shall remain within the elastic range under service and fatigue level loading conditions.

- Maximum cover plate vertical deflection is limited to 0.070” under service loading and 0.035” under fatigue loading at maximum opening width, excluding seismic. Seismic slide plate system is allowed to become inelastic for maximum joint opening, including seismic movement under all loading conditions. The system is designed such that the slide plate remains in place and viable during and after a seismic event.

- All stresses related to fatigue resistance and endurance limits are within the design limit criteria of the seismic slide plate expansion joint system.

  - Components and Materials

A.	Base Member - capable of AASHTO HS-20 loading from aluminum alloy 6005-T5.

B.	Extension Plates - 3/16 inch minimum plate thickness from aluminum alloy 6005-T5. Recessed extension plates allow the seismic slide plate cover to remain flush with finished deck surface during thermal movement.

- Aluminum Slide Plate Cover (standard) - 3/8 inch minimum plate thickness from aluminum alloy 6005-T5 with no-bump inverted beveled edges. Top of cover shall shall be flush with the finished floor surface.

- Stainless Steel Slide Plate (custom) – contact manufacture for design options.

- Seismic Centering Bar Device – shall have solid aluminum circular ball ends that lock and slide in the base member and rotate freely. Provide stainless steel hardware connected through rubber impact dampers and heavy-duty coil displacement spring. The device shall firmly secure the slide plate covers while allowing it to displace and return to its natural position after a seismic occurrence. Spacing shall be no greater than 18 inches unless less spacing is required for project specific requirements.

- Rubber Gutter – continuous fabric reinforced 60-mil EPDM rubber adhered to concrete floor with MicroWaterSeal Tape adhesive and secured with the aluminum base frame. The rubber gutter drains excess moisture through an optional tube assembly when detailed on the drawings.

- Accessories – provide necessary hardware required for complete installation.

- Blockout Infill Material – provide LokCrete( elastomeric concrete blockout infill material as manufactured by MM Systems Corporation. Elastomeric concrete shall be produced in an ISO2001 manufacturing facility consisting of polyurethane liquid components “A” and “B” and a specialty aggregate component “C”.  LokCrete( cures exothermically and bonds to concrete and aluminum.

Physical Properties of Elastomeric concrete binder after seven-day cure at room temperature:

##### Property				Requirement	           ASTM Method

Tensile Strength			4750 psi		D412

Compressive strength			9200 psi 		D695

Ultimate Elongation			10% 			D412

Hardness, Shore D			78 +/- 5		D2240

Tear Resistance			200 pli / 35 kN/m	D624

Water Absorption			3%			D570

Heat Shrinkage, max.			2%			D1299

Compression Set			48%			D395

Pot Life				25 minutes 		(after mixing)

Physical Properties of Elastomeric concrete binder & aggregate mix:

##### Property				Requirement             	ASTM Method

Compressive strength			2800 psi 		D695

Resilience @ 5% deflection		95%			D695

Compressive stress, psi		800 psi min.		D695

Impact resistance, ft-lb, @ -20(F	No Cracks		Ball drop

Adhesion				Concrete Failure	D421

  - Life Safety – Fire Barrier Systems (as required)

- Approved PyroFlex( Fire Barrier Systems (PF Series), as manufactured by MM Systems Corporation. Supply fire-resistive barrier systems that have ratings equal to or greater than the rating of adjacent construction when tested in accordance with ASTM E1966 and ASTM E119. Provide specified (2, 3 or 4 hour) rated fire barrier expansion joint assembly.

- Fire Barrier System shall be capable of anticipated movement and maintain fire rating through precondition cycling and fire performance testing in accordance with ASTM E1966. System shall have factory and field splices tested in accordance with ASTM E1966.  Manufacturer shall provide field-splicing instructions.

- Fire Barrier System shall have been tested in accordance with ASTM E1966 at a maximum joint opening as defined by ASTM E1399 which meets or exceeds the maximum joint opening required by the project design requirements. System and manufacturer shall be listed with an accredited independent laboratory.

  - Fabrication

- Metal Frames and Plates – base frames shall be shipped in standard 10 foot lengths and slide plate covers shall be shipped in longest available mill lengths. All profiles shall be cut to length at jobsite and miter cut where required in the field to conform to directional changes.

- Rubber Gutter – shall be shipped in the longest practical continuous length in manufacturer’s standard shipping carton.

- Elastomeric Concrete Blockout Infill Material – Ship in manufacturer’s approved containers shrink wrapped on wooden pallets.

- Wall Mount (floor-to-wall condition) – aluminum ball and socket extrusions shall be shipped in standard 10 ft. lengths and shall be cut to length on jobsite where required.

- Fire Barriers (as required) – Ship manufacturer’s standard assembly for the required hourly rating with ends prepared for field splicing.  Assemblies shall be miter cut in the field to accommodate changes in direction.

  - Finishes

- Aluminum Slide Plates - top surface of aluminum slide plate shall be standard mill finish.

- Recessed Extension Plates shall be standard mill finish.

- Elastomeric Concrete Blockout Filler (as required) - shall be supplied in standard black or custom gray colors.

## PART 3 – EXECUTION

  - Installation

- Preparation of the Work Area

- The contractor shall provide properly formed concrete blockouts and expansion joint openings constructed to the exact dimensions and elevations shown on manufacturer’s standard system drawings or as shown on the contract drawings. Deviations from these dimensions will not be allowed without the written consent from the engineer of record.

- Actual field conditions of existing expansion joint blockouts may be deeper and wider than the proposed new expansion joint system as detailed on the contract drawings. Blockout size shall be corrected by filling it with an approved structural concrete patching material or elastomeric concrete. When blockout size is smaller it shall be made larger by saw cutting.

- The base of the blockout recess must be formed level and at the same elevation across the joint. Any edge or area in need of repair shall utilize structural concrete repair materials.

- Surface areas two feet on each side of the expansion joint opening shall be finish grade concrete perpendicular to joint opening creating flush floor-to-floor transition.  Elevations on each side shall be identical.

- Install expansion joint system in strict accordance with the manufacturer's typical details and instructions along with the advice of their qualified representative. Refer to Manufacturers Installation Guide for step-by-step installation instructions.

- Elastomeric Concrete Installation

- The contractor shall clean the concrete blockout of all contaminants by sandblasting immediately prior to installation of expansion joint system.  Concrete form release agents, water repellents, laitance, surface dirt, rust, old sealants and other surface treatments and protective coatings must be removed from the blockout substrate surface in order to obtain the proper elastomeric concrete bond.

- Do not install elastomeric concrete until the concrete has been air-dried at temperatures at or above 45 degrees F. for a minimum of 28 days. The concrete must have a measured moisture content that is below 4 percent. The blockout area must be completely dry prior to placement of the elastomeric concrete.  Blockouts requiring the use of structural repair materials must be cured as per manufactures recommendation.  Blow out the area thoroughly using compressed air.

- Refer to Manufacturers Installation Guide for detailed step-by-step instructions on how to properly mix and place elastomeric concrete filler.

- IMPORTANT - Premature exposure to traffic can cause stress on the bond line related to vertical slab deflection. For best results wait a minimum of 24 hours (depending on temperature and humidity) before allowing vehicular traffic to drive over the system (contact manufacturer if faster opening time is required).

  - Clean and Protect

- Protect the system and its components during construction.  Heavy construction vehicles will not be permitted to cross the expansion joint. Subsequent damage to the expansion joint system will be repaired at the general contractor’s expense.

- After work is complete, clean exposed surfaces with a suitable cleaner that will not harm or attack the finish of the concrete or system.

END OF SECTION