SPECIFICATION

Sections 05810 / 07102 / 07915

Seismic Top-mount Slide Plate System

###### STS Series - Traffic Bearing Expansion Joint

# PART 1 – GENERAL

  - Work Included

- The work shall consist of furnishing and installing seismic expansion joints in accordance with the details shown on the plans and the requirements of the specifications.  The expansion joints utilize a surface mounted seismic slide plate that glides on the finished deck surface. A seismic centering device with impact dampeners and tension springs allow the slide plate to remain firmly in place throughout a seismic occurrence. Watertightness is achieved through an integral flexible fabric reinforced rubber gutter in addition to a waterstop that provides impact resistance and sound dampening.

- Related Work

- Section 03300 - Cast-in-place concrete

- Section 05500 - Miscellaneous metal / expansion joints

- Section 07600 - Flashing and sheet metal

- Section 07900 - Sealants, caulking and waterproofing

  - Submittals

- General – Submit the following according to Division 1 Specification Section.

- Standard Drawings – Submit typical expansion joint drawings indicating pertinent dimensions, general construction, blockout dimensions and product information.

  - Product Delivery, Storage and Handling

- Deliver products to site in Manufacturer’s original, intact, labeled containers and store under cover in a dry location until installed.  Store off the ground in temperatures above 40ºF, protect from weather and construction activities.

  - Basis of Design

- All joints shall be designed to meet the specified performance criteria of the project as manufactured by MM Systems Corp., 50 MM Way, Pendergrass, GA, 30567 / Tel. 866.506.6929 / Fax. 706.824.7501 / Web www.mmsystemscorp.com

- Alternate manufacturers will not be considered for this project due to insufficient product evaluation time. Submit for future evaluation, products that meet the design criteria and exhibit performance features that are equal to or superior to those called for in the base product specification. Submittal of alternates must be made two weeks prior to bid opening on future projects to allow proper evaluation time. Alternate products not adhering to all listed design features will not be considered. Final decision will be at the sole discretion of the architect or consulting engineer.

- Submit verifiable list of prior installations, along with owner contact information, showing successful experience with the proposed systems that must incorporate solid aluminum seismic centering devices (centering bars) and rubber dampeners that provide impact, sound and water infiltration resistance.

## Quality Assurance

- Pre-construction – the General Contractor, Engineer/Architect, Concrete Subcontractor, Manufacturer’s Representative and Certified Contractor, will conduct a pre-construction meeting to discuss blockout construction, joint gap settings and construction phasing. This meeting shall be held prior to any concrete placement at expansion joint blockouts and may be held in conjunction with the concrete pre-pour meeting.

- Joint Opening Adjustment – the Project Engineer shall provide calculations to the concrete subcontractor to adjust the nominal joint opening the day of the concrete placement. Use a “temperature adjustment table” with expansion joint openings calculated in five (5ºF) degree increments based on a temperature range of [adjust for project] -20ºF to 120ºF.

- Expansion Joint Blockouts - shall be floated and troweled before final cure to remove all air pockets, voids and spalls caused by formwork.

- Leveling Bed - comprised of structural grout is recommended to compensate for elevation changes along the length of the expansion joint. This will require the blockout depth to be set below the 1-7/8 inch system height.

- Expansion Joint Surface Areas - two feet on each side of joint gap shall be finished and graded perpendicular to joint gap creating flush slab-to-slab transition.  Elevations on each side of the joint opening shall be identical.

- Pre-installation Inspection – the General Contractor, Engineer/Architect, Manufacturer’s Representative and Certified Contractor, will conduct a pre-installation project site inspection. The General Contractor shall provide a field report that summarizes the project conditions and any remedial action necessary to correct field conditions (substrate, joint size, blockout, vertical offsets, etc.) that may affect expansion joint system performance.

- Service Condition - insure that anticipated service conditions (loads, speed of traffic, movement, vertical offsets, turning lanes, etc) are part of the expansion joint system selection criteria.

- Certification / Installation – a factory-trained and “certified” contractor shall install the specified expansion joint system. The contractor shall provide proof of certification from manufacturer and proof of participation in manufacturer’s continuing education program.

- Warranty – the Manufacturer and Certified Contractor jointly warrant to the Owner that the expansion joint system shall be free from manufacturing, material and installation defects for a period of two (2) years from the date of installation, based on specified movements and design conditions for normal traffic use as recommended by the National Parking Association’s “Parking Facility Maintenance Manual” and subject to the terms and conditions of the manufacturer’s standard written limited warranty. The Certified Contractor and Manufacturer will jointly warrant and provide at no charge, all materials and labor needed to properly repair defective expansion joint within the term of the warranty. No liability or responsibility is accepted due to defects in the concrete.

## PART 2 – PRODUCT

  - General

- Provide seismic expansion joint sealing system that meets the specified movement requirements and is capable of HS-20 loading and able to accommodate vehicular and pedestrian traffic.

- System shall consist of recessed extension plates that allow a seismic slide plate to remain flush with finished deck surface. Provide a seismic centering bar device with impact dampeners and displacement springs to allow the slide plate to displace and return to its natural position after a seismic occurrence. Include an integral waterstop that provides impact resistance and sound dampening.

- Furnish approved Seismic Top-mount Slide Plate System “STS Series” as manufactured by MM Systems Corporation.

- Select the system size at each joint location based on the movement and design requirements that meet the project specification or as defined by the structural engineer of record.

- The Certified Contractor must provide written confirmation, utilizing manufacturer’s product data, that the model and size selected will comply with and accommodate expansion, contraction, vertical displacement and lateral shear throughout the full movement cycle.

  - Components and Materials

  - Base Member - capable of HS-20 loading from aluminum alloy 6005 -T5.

- Aluminum Slide Plate (standard) - 3/8” minimum plate thickness from aluminum alloy 6005 -T5 with ADA compliant beveled edges (12 inch opening requires 1/2 inch aluminum plate). Top surface shall provide slip reistant V-groove finish. Underside of plate shall have continuous end cavities to receive integral high-density rubber waterstop that provides impact resistance and sound dampening.

- Stainless Steel Slide Plate (special order) - for openings greater than 12 inches provide 3/8” [or 1/2 inch thick – dependent on deflection requirements] thick stainless steel plate with standard mill finish. Slide plate must have ADA compliant beveled edges.

- Seismic Centering Bar Device - shall have solid aluminum circular ball ends that lock and slide in the base member and rotate freely. Provide stainless steel hardware connected through rubber impact dampeners and single or dual heavy-duty displacement springs.

- Rubber Gutter - continuous fabric reinforced 60-mil EPDM rubber attached into an integral cavity in the base member. Provide flexible down spout and drain tubes as required. Fastener penetrations in the gutter are not allowed.

- Accessories - Provide necessary assembly hardware required for complete installation.

- Waterproofing (when specified) – provide LokCrete( elastomeric concrete header material as manufactured by MM Systems Corporation. Elastomeric concrete shall be produced in an ISO2001 manufacturing facility consisting of polyurethane liquid components “A” and “B” and a specialty aggregate component “C”.  LokCrete( cures exothermically and bonds to concrete, aluminum and steel.

Physical Properties of Elastomeric concrete binder after seven-day cure at room temperature:

##### Property				Requirement	           ASTM Method

Tensile Strength			4750 psi		D412

Ultimate Elongation			10% 			D412

Hardness, Shore D			78 +/- 5		D2240

Tear Resistance			200 pli / 35 kN/m	D624

Water Absorption			3%			D570

Heat Shrinkage, max.			2%			D1299

Compression Set			48%			D395

Pot Life				5 minutes 		(after mixing)

Physical Properties of Elastomeric concrete binder & aggregate mix:

##### Property				Requirement             	ASTM Method

Compressive strength			9200 psi 		D695

Resilience @ 5% deflection		95%			D695

Compressive stress, psi		800 psi min.		D695

Impact resistance, ft-lb, @ -20(F	No Cracks		Ball drop

Adhesion				Concrete Failure	D421

  - Life Safety – Fire Barrier Systems (as required)

- Approved PyroFlex( Fire Barrier Systems (PF Series), as manufactured by MM Systems Corporation - Supply fire-resistive barrier systems that have ratings equal to or greater than the rating of adjacent construction when tested in accordance with ASTM E1966 and ASTM E119. Provide specified (2, 3 or 4 hour) rated fire barrier expansion joint assembly.

- Fire Barrier System shall be capable of anticipated movement and maintain fire rating through precondition cycling and fire performance testing in accordance with ASTM E1966. System shall have factory and field splices tested in accordance with ASTM E1966.  Manufacturer shall provide field-splicing instructions.

- Fire Barrier System shall have been tested in accordance with ASTM E1966 at a maximum joint opening as defined by ASTM E1399 which meets or exceeds the maximum joint opening required by the project design requirements. System and manufacturer shall be listed with an accredited independent laboratory.

  - Fabrication

- Metal Frames and Plates – shall be shipped in standard 10 ft. lengths and shall be cut to length at jobsite where required. All profiles shall be miter cut in the field to conform to directional changes unless otherwise contracted with expansion joint manufacturer.

- Rubber Gutter – shall be shipped in the longest practical continuous length in manufacturer’s standard shipping carton.

- Elastomeric Concrete Blockout Filler – Ship in manufacturer’s approved containers shrink wrapped on wooden pallets.

- Wall Mount (slab-to-wall condition) – aluminum ball and socket extrusions shall be shipped in standard 10 ft. lengths and shall be cut to length on jobsite where required.

- Fire Barriers (if required) – Ship manufacturer’s standard assembly for the required hourly rating with ends prepared for field splicing.  Assemblies shall be miter cut in the field to accommodate changes in direction.

  - Finishes

- Aluminum Plates (standard) - top surface of aluminum slide plate shall have slip resistant V-groove profile and standard mill finish. Extension plates shall be standard mill finish.

- Stainless Steel Plates (custom) - top surface of stainless steel slide plate shall be standard mill finish.

- Elastomeric Concrete Blockout Filler (as required) - shall be supplied in standard black or custom gray colors.

## PART 3 – EXECUTION

  - Installation

- Preparation of the Work Area

- The contractor shall provide properly formed concrete blockouts and expansion joint openings constructed to the exact dimensions and elevations shown on manufacturer’s standard system drawings or as shown on the contract drawings. Deviations from these dimensions will not be allowed without the written consent.

- Actual field conditions of existing expansion joint blockouts may be deeper and wider than the proposed new expansion joint system as detailed on the contract drawings. Blockout size shall be corrected by filling it with an approved structural concrete patching material or elastomeric concrete. When blockout size is smaller it shall be made larger by saw cutting.

- The base of the blockout recess must be formed level and at the same elevation across the joint. Any edge or area in need of repair shall utilize structural concrete repair materials.

- Surface areas two feet on each side of the expansion joint opening shall be finish graded flat and perpendicular to joint opening creating flush slab-to-slab transition.  Elevations and flatness on each side shall be identical to allow the STS Slide Plate to move without restriction.

- Install expansion joint system in strict accordance with the manufacturer's typical details and instructions along with the advice of their qualified representative. Refer to Manufacturers Installation Guide for detailed step-by-step installation instructions.

- Elastomeric Concrete Blockout Filler Installation (when specified)

- The contractor shall clean the concrete blockout of all contaminants by sandblasting immediately prior to installation of expansion joint system.  Concrete form release agents, water repellents, laitance, surface dirt, rust, old sealants and other surface treatments and protective coatings must be removed from the blockout substrate surface in order to obtain the proper elastomeric concrete bond.

- Do not install elastomeric concrete until the concrete has been air-dried at temperatures at or above 45 degrees F. for at least 28 days minimum and the concrete must have a measured moisture content that is below 4 percent. The blockout area must be completely dry prior to placement of the elastomeric concrete.  Blockouts requiring the use of structural repair materials must be cured according to the manufacturers directions.  Blow out the area thoroughly using compressed air.

- Refer to Manufacturers Installation Guide for detailed step-by-step instructions on how to properly mix and install elastomeric concrete filler.

- IMPORTANT - Premature exposure to vehicular traffic can cause stress on the bond line related to vertical slab deflection. For best results wait a minimum of 24 hours (depending on temperature and humidity) before allowing vehicular traffic to drive over the system (contact manufacturer if faster opening time is required).

  - Clean and Protect

- Protect the system and its components during construction.  Heavy construction vehicles will not be permitted to cross the expansion joint. Subsequent damage to the expansion joint system will be repaired at the general contractor’s expense. After work is complete, clean exposed surfaces with a suitable cleaner that will not harm or attack the finish.

END OF SECTION