SPECIFICATION

Sections 07 90 00 / 07 95 00

(Formerly sections 05810 / 07102 / 07915)

Vertical Sealing System - VSS Series

(Waterproof Expansion Joint Sealing System)

# PART 1 – GENERAL

  - Work Included

- The work shall consist of furnishing and installing vertical expansion joints in accordance with the details shown on the plans and the requirements of the specifications.  The expansion joints utilize extruded elastoprene seals bonded to the structural concrete joint opening.

- Related Work

- Section 03300 - Cast-in-place concrete

- Section 05500 - miscellaneous metal / expansion joints

- Section 07600 - Flashing and sheet metal

- Section 07900 - Sealants, caulking and waterproofing

  - Submittals

- General – Submit the following according to Division 1 Specification Section.

- Standard Drawings – Submit typical vertical expansion joint drawings(s) indicating pertinent dimensions, general construction, joint opening dimensions and product information.

  - Product Delivery, Storage and Handling

- Deliver products to site in Manufacturer’s original, intact, labeled containers and store under cover in a dry location until installed.  Store off the ground in temperatures above 40ºF, protect from weather and construction activities.

  - Basis of Design

- All joints shall be designed to meet the specified performance criteria of the project as manufactured by MM Systems Corp., 50 MM Way, Pendergrass, GA, 30567 Tel. 800.241.3460 Fax. 706.824.7501 / Web www.mm-usa.com

- Alternate manufacturers will not be considered for this project due to insufficient product evaluation time. Submit for future evaluation, products that meet the design criteria and exhibit performance features that are equal to or superior to those called for in the base product specification. Submittal of alternates must be made two weeks prior to bid opening on future projects to allow proper evaluation time. Alternate products not adhering to all listed design features will not be considered.

## Quality Assurance

- Pre-construction – the General Contractor, Engineer/Architect, Concrete Subcontractor, Manufacturer’s Representative and Certified Contractor, will conduct a pre-construction meeting to discuss joint gap construction, joint width settings and construction phasing. This meeting shall be held prior to any substrate placement at expansion joint locations.

- Joint Opening Adjustment – the Project Engineer shall provide calculations to the concrete subcontractor to adjust the nominal joint opening the day of the concrete placement. Use a “temperature adjustment table” with expansion joint openings calculated in five (5ºF) degree increments based on a temperature range of [adjust for project] -20ºF to 120ºF.

- Pre-installation Inspection – the General Contractor, Engineer/Architect, Manufacturer’s Representative and Certified Contractor, will conduct a pre-installation project site inspection. The General Contractor shall provide a field report that summarizes the project conditions and any remedial action necessary to correct field conditions (substrate, joint size, parallel sidewalls, vertical offsets, etc.) that may impact expansion joint system performance.

- Certification / Installation – a factory trained and “certified” contractor shall install the specified expansion joint system. The contractor shall provide proof of certification from manufacturer and proof of participation in manufacturer’s continuing education program.

- Warranty – the Manufacturer and Certified Contractor jointly warrant to the Owner that the expansion joint system shall be free from manufacturing, material and installation defects for a period of one (1) year from the date of installation, based on specified movements and design conditions for normal use and subject to the terms and conditions of the manufacturer’s standard written limited warranty. The Certified Contractor and Manufacturer shall provide at no charge, all materials and labor needed to properly repair defective expansion joint within the term of the warranty. No liability or responsibility is accepted due to defects in the concrete or surrounding substrate.

## PART 2 – PRODUCT

  - General

- Provide watertight vertical expansion joint sealing system that meets the specified thermal movement requirements and is capable of accommodating seismic movement.

- System shall consist of a continuous elastoprene primary rubber visual seal and a secondary moisture barrier that snap locked into aluminum mounting frames. Seismic applications shall utilize a pantograph-centering device. The rubber seal must include steel reinforced splice connections.

- Furnish approved Vertical Sealing System “VSS Series” as manufactured by MM Systems Corporation.

- Select the system size at each joint location based on the movement and design requirements that meet the project specification or as defined by the structural engineer of record.

- The Certified Contractor must provide written confirmation, utilizing manufacturer’s product data insuring the model and size selected will comply with and accommodate expansion, contraction, displacement and lateral shear throughout the full movement cycle.

  - Components and Materials

- Visual Rubber Seal – Material shall be a flexible, extruded thermoplastic elastoprene rubber compound exhibiting the physical properties listed in the table below.  The seal design shall have locking lugs that snap into aluminum mounting frames.

PHYSICAL PROPERTIES OF ELASTOPRENE RUBBER SEAL:

Property			         Requirement	         ASTM Method

Tensile Strength		     	1000 psi (+75/-0)	D412

Ultimate Elongation			445%			D412

Hardness, Shore A			65 +/- 3 pts.		D2240

Tear Strength		140 pli / 24.5 kN/m @ 23(C		D624

58 pli / 10.2 kN/m @100(C		D624

Compression set

168 hrs.			25% @ 23(C		D395

168 hrs.			38% @ 100(C		D395

Ozone Resistance			No Cracks		D1149

UV Resistance			Very Good

Brittle Point				-76(F(-60(C)		D746

- Secondary Moisture Barrier - elastomeric moisture barrier shall be designed utilizing a serpentine configuration allowing maximum movement and flexibility.  Provide side lugs that mechanically lock into a corresponding aluminum profiles.  Seismic systems with pantograph assemblies shall utilize a Lexsuco Moisture Barrier System.

- Mounting Frame - snap lock design made from aluminum alloy 6005 -T5.

- Accessories - provide necessary assembly hardware required for complete installation.

  - Life Safety – Fire Barrier Systems (as required)

- Approved PyroFlex( Fire Barrier Systems (PF Series), as manufactured by   MM Systems Corporation - Supply fire-resistive barrier systems that have ratings equal to or greater than the rating of adjacent construction when tested in accordance with ASTM E1966 and UL 2079. Provide specified [2, 3 or 4 hour] rated fire barrier expansion joint assembly.

- Fire Barrier System shall be capable of anticipated movement and maintain fire rating through precondition cycling and fire performance testing in accordance with ASTM E1966. System shall have factory and field splices tested in accordance with ASTM E1966.  Manufacturer shall provide field-splicing instructions.

Fire Barrier System shall have been tested in accordance with ASTM E1966 at a maximum joint opening as defined by ASTM E1399 which meets or exceeds the maximum joint opening required by the project design requirements. System and manufacturer shall be listed with an accredited independent laboratory.

  - Fabrication

- Elastoprene Rubber Seal - ship in the longest practical continuous length coiled on manufacturer’s standard reel or in cartons.

- Secondary Moisture Barrier - ship in the longest practical continuous length on manufacturer’s standard reel or in cartons.

- Metal Mounting Frame - ship in standard 10 ft. lengths and shall be cut to length at jobsite where required. All profiles shall be miter cut in the field to conform to directional changes unless otherwise contracted with expansion joint manufacturer. All anchor holes shall be field drilled in accordance with manufacturer’s drawings.  Spacing shall be a maximum of 18” o.c.

- Pantograph Control Mechanism (where required) - provide factory assembled equidistant centering mechanisms ready for field installation.

- Fire Barriers (as required) - ship manufacturer’s standard assembly for the required hourly rating with ends prepared for field splicing.  Assemblies shall be miter cut in the field to accommodate changes in direction.

  - Finishes

- Elastoprene rubber seal shall be supplied in standard colors black, beige or gray.

- Contact manufacturer for custom colors or color matching to match the project requirements.

- Aluminum mounting frames shall be supplied in standard mill finish.

## PART 3 – EXECUTION

  - Installation

- Preparation of the Work Area

- The contractor shall provide properly formed and sized expansion joint openings constructed to the exact dimensions shown on manufacturer’s standard system drawings or as shown on the contract drawings.

- The contractor shall insure that the joint opening sidewall interfaces run parallel to each other for the entire length of the joint.  Sidewalls should be plumb and interfaces must be continuously equidistant from each other across the joint width to accommodate the proper installation of the expansion joint sealing system.

- The contractor shall provide proper and adequate adjacent construction to receive and support the vertical expansion joint system.  The supporting framework shall be of proper design to rigidly secure all anchors and hardware to insure proper installation and function of the joint system.

- Installation of Vertical Expansion Joint System

- Attach aluminum wall frames to substrate using required hardware. Apply silicone or polyurethane sealant (supplied by installer) to seal the back side of the frame to the wall substrate.

- Uncoil the seal and allow it to relax to relieve any temporary coiling from shipment packaging.  The seal shall be cut to the correct length without pulling or exerting excess tension.

- Field Seal Splices and Mitered Directional Changes – provide steel pin reinforced directional changes for 90( corners, tees and crosses. Utilize Elastobond Activator and Rubber Splice Adhesive to insure that all external webs of the seal profile are properly bonded at all splice locations.

- Apply silicone or polyurethane sealant (supplied by installer) intermittently per the manufacturer’s instructions into the snap-lock cavities.

- Insert seal into the snap-lock lugs of the aluminum wall frames. Utilize blunt installation tool to properly position the seal.

- After proper positioning of the seal, clean all excess sealant around the edges and top of the joint.

- Refer to Manufacturers Installation Guide for step-by-step instructions.

  - Clean and Protect

- Protect the system and its components during construction. Subsequent damage to the expansion joint system will be repaired at the general contractor’s expense. After work is complete, clean exposed surfaces with a suitable cleaner that will not harm or attack the elastoprene seal finish.

END OF SECTION